## Sheet1
Input Parameters |  | Intermediate Parameters |  | Outputs
Primary Voltage (kV) | 34.5 | Secondary Turns | 1141 | copper loss (total, W) | 4477.4615
Secondary Voltage (kV) | 25 | Primary Current (efficiency ignored) | 14.4928 | core loss (W) | 3094.7257
Power (kVA) | 500 | Secondary Current (efficiency ignored) | 20 | TOTAL LOSS | 7.5722
Max Ambient Temp | 50 | Core Area (cm2) | 657.8007 | EFFICIENCY | 0.98508
Max Coil Temp | 80 | Core depth (cm) | 25.6476 | Copper Cost | 771.088
frequency | 50 | MLT (cm) | 107.72 | Core Cost | 8181.4587
current density (A/mm2) | 4 | primary conducter crossection (mm2) | 3.6232 | efficiency cost (20 years, capacity factor=0.5) | 132664.7185
Bmax (T) | 1.5 | secondary conducter crossection (mm2) | 5 | TOTAL COST | 141617.2652
core loss (W/kg) | 0.87
lamination factor | 0.95 | Window Area (cm2) | 22823.0435
rho Copper at 100C (ohm*m/mm2) | 0.022762 | core volume (m3) | 0.46499
Fill Factor | 0.5 | core weight | 3557.1559
density of the copper (kg/m3) | 8960 | Conductor length (primary, m) | 1696.5904
density of the core material(kg/m3) | 7650 | Conductor length (secondary, m) | 1229.0855
Copper cost ($/kg) | 7 | Rp(ohm) | 10.6586
Core material cost ($) | 2.3 | primary conductor weight | 55.0777
|  | secondary conductor weight | 55.0777
Primary Number of Turns | 1575 | Llk | 5%
Lmagnetizing